## symptoms
index | Symptoms | Possible Causes
1 | Pump does not deliver liquid | 1/2/3/5/10/12/13/14/16/21/22/25/30/32/38/40
2 | Insufficient capacity delivered | 2/3/4/5/6/7/7a/10/11/12/13/14/15/16/17/18/21/22/23/24/25/31/32/40/41/44/63/64
3 | Insufficient pressure developed | 4/6/7/7a/10/11/12/13/14/15/16/18/21/22/23/24/25/34/39/40/41/44/63/64
4 | Pump loses prime after starting | 2/4/6/7/7a/8/9/10/11
5 | Pump requires excessive power | 20/22/23/24/26/32/33/34/35/39/40/41/44/45/61/69/70/71
6 | Pump vibrates or is noisy at all flows | 2/16/37/43/44/45/46/47/48/49/50/51/52/53/54/55/56/57/58/59/60/61/67/78/79/80/81/82/83/84/85
7 | Pump vibrates or is noisy at low flows | 2/3/17/19/27/28/29/35/38/77
8 | Pump vibrates or is noisy at high flows | 2/3/10/11/12/13/14/15/16/17/18/33/34/41
9 | Shaft oscillates axially | 17/18/19/27/29/35/38
10 | Impeller vanes are eroded on visible side | 3/12/13/14/15/17/41
11 | Impeller vanes are eroded on invisible side | 12/17/19/29
12 | Impeller vanes are eroded at discharge near centre | 37
13 | Impeller vanes are eroded at discharge near shrouds or at shroud/vane fillets | 27/29
14 | Impeller shrouds bowed out or fractured | 27/29
15 | Pump overheats and seizes | 1/3/12/28/29/38/42/43/45/50/51/52/53/54/55/57/58/59/60/61/62/77/78/82
16 | Internal parts are corroded prematurely | 66
17 | Internal clearances wear too rapidly | 3/28/29/45/50/51/52/53/54/55/57/59/61/62/66/77
18 | Axially split casing is cut through wire-drawing | 63/64/65
19 | Internal stationary joints are cut through wire-drawing | 53/63/64/65
20 | Packed box leaks excessively or packing has short life | 8/9/45/54/55/57/68/69/70/71/72/73/74
21 | Packed box sleeve is scored | 8/9
22 | Mechanical seal leaks excessively | 45/54/55/57/58/62/75/76
23 | Mechanical seal has damaged faces, sleeve bellows | 45/54/55/57/58/62/75/76
24 | Bearings have short life | 3/29/41/42/45/50/51/54/55/58/77/78/79/80/81/82/83/84/85
25 | Coupling fails | 45/50/51/54/67

## causes
index | trouble_type | causes
1 | Suction Troubles | Pump not primed
2 | Suction Troubles | Pump suction pipe not completely filled with liquid
3 | Suction Troubles | Insufficient available NPSH
4 | Suction Troubles | Excessive amount of air of gas in liquid
5 | Suction Troubles | Air pocket in suction line
6 | Suction Troubles | Air leaks into suction line
7 | Suction Troubles | Air leaks into pump through stuffing boxes or through mechanical seal
7a | Suction Troubles | Air in source of sealing liquid
8 | Suction Troubles | Water seal pipe plugged
9 | Suction Troubles | Seal cage improperly mounted in stuffing box
10 | Suction Troubles | Inlet of suction pipe insufficiently submerged
11 | Suction Troubles | Vortex formation at suction
12 | Suction Troubles | Pump operated with closed or partially closed suction valve
13 | Suction Troubles | Clogged suction strainer
14 | Suction Troubles | Obstruction in suction line
15 | Suction Troubles | Excessive friction losses in suction line
16 | Suction Troubles | Clogged impeller
17 | Suction Troubles | Suction elbow in plane parallel to the shaft (for double-suction pumps)
18 | Suction Troubles | Two elbows in suction piping at 90º to each other, creating swirl and pre-rotation
19 | Suction Troubles | Selection of pump with too high a suction specific speed
20 | Other Hydraulic Problems | Speed of pump too high
21 | Other Hydraulic Problems | Speed of pump too low
22 | Other Hydraulic Problems | Wrong direction of rotation
23 | Other Hydraulic Problems | Reverse mounting of double-suction impeller
24 | Other Hydraulic Problems | Uncalibrated instruments
25 | Other Hydraulic Problems | Impeller diameter smaller than specified
26 | Other Hydraulic Problems | Impeller diameter larger than specified
27 | Other Hydraulic Problems | Impeller selection with abnormally high head coefficient
28 | Other Hydraulic Problems | Running the pump against a closed discharge valve without opening a bypass
29 | Other Hydraulic Problems | Operating pump below recommended minimum flow
30 | Other Hydraulic Problems | Static head higher than shut-off head
31 | Other Hydraulic Problems | Friction losses in discharge higher than calculated
32 | Other Hydraulic Problems | Total head of system higher than design of pump
33 | Other Hydraulic Problems | Total head of system lower than design of pump
34 | Other Hydraulic Problems | Running of pump at too high a flow (for low specific speed pumps)
35 | Other Hydraulic Problems | Running pump at too low a flow (for high specific speed pumps)
36 | Other Hydraulic Problems | ----
37 | Other Hydraulic Problems | Too close a gap between impeller vanes and volute tongue or diffuser vanes
38 | Other Hydraulic Problems | Parallel operation of pumps unsuitable for the purpose
39 | Other Hydraulic Problems | Specific gravity of liquid differs from design conditions
40 | Other Hydraulic Problems | Viscosity of liquid differs from design conditions
41 | Other Hydraulic Problems | Excessive wear at internal running clearances
42 | Other Hydraulic Problems | Obstruction in balancing device leak-off line
43 | Other Hydraulic Problems | Transients at suction source (imbalance between pressure at surface of liquid and vapour pressure at suction flange)
44 | Mechanical Troubles - General | Foreign matter in impellers
45 | Mechanical Troubles - General | Misalignment
46 | Mechanical Troubles - General | Foundation insufficiently rigid
47 | Mechanical Troubles - General | Loose foundation bolts
48 | Mechanical Troubles - General | Loose pump or motor bolts
49 | Mechanical Troubles - General | Inadequate grouting of baseplate
50 | Mechanical Troubles - General | Excessive piping forces and movements on pump nozzles
51 | Mechanical Troubles - General | Improperly mounted expansion joints
52 | Mechanical Troubles - General | Starting the pump without proper warm-up
53 | Mechanical Troubles - General | Mounting surfaces of internal fits (at wearing rings, impellers, shaft sleeves, shaft nuts, bearing housings, etc) not perpendicular to shaft axis
54 | Mechanical Troubles - General | Bent shaft
55 | Mechanical Troubles - General | Rotor out of balance
56 | Mechanical Troubles - General | Parts loose on the shaft
57 | Mechanical Troubles - General | Shaft running off-centre because of worn bearings
58 | Mechanical Troubles - General | Pump running at or near critical speed
59 | Mechanical Troubles - General | Too long a shaft span or too small a shaft diameter
60 | Mechanical Troubles - General | Resonance between operating speed and natural frequency of foundation, baseplate or piping
61 | Mechanical Troubles - General | Rotating part rubbing on stationary part
62 | Mechanical Troubles - General | Incursion of hard solid particles into running clearances
63 | Mechanical Troubles - General | Improper casing gasket material
64 | Mechanical Troubles - General | Inadequate installation of gasket
65 | Mechanical Troubles - General | Inadequate tightening of casing bolts
66 | Mechanical Troubles - General | Pump materials not suitable for liquid handled
67 | Mechanical Troubles - General | Certain couplings lack lubrication
77 | Mechanical Troubles - Bearings | Excessive radial thrust in single-volute pumps
78 | Mechanical Troubles - Bearings | Excessive axial thrust caused by excessive wear at internal clearances or by failure or, if used,
79 | excessive wear of balancing device | Wrong grade of grease or oil
80 | excessive wear of balancing device | Excessive grease or oil in anti-friction bearing houses
81 | excessive wear of balancing device | Lack of lubrication
82 | excessive wear of balancing device | Improper installation of anti-friction bearings such as damage during installation, incorrect assembly of stacked bearings, use of unmatched bearings as a pair, etc
83 |  | Dirt getting into bearings
84 |  | Moisture contaminating lubricant
85 |  | Excessive cooling of water-cooled bearings

## all_pumps
pump type | Fault | Cause | Remedy or Action
Centrifugal Pump | Pump not turning | Driver not running | Check fuses, circuit breakers
Centrifugal Pump | Pump not turning | Keys sheared | Replace
Centrifugal Pump | Pump not turning | Drive belt slip | Check and adjust
Centrifugal Pump | Pump not turning | Coupling fault | Check if slipping or broken, replace if necessary
Centrifugal Pump | Pump not turning | Shaft or gears sheared | Check, replace if necessary
Centrifugal Pump | Pump not priming | Inlet valve closed | Open valve
Centrifugal Pump | Pump not priming | Inlet clogged or restricted | Check and clear
Centrifugal Pump | Pump not priming | Air leaks on suction side | Replace seals, check line(s) for leaks
Centrifugal Pump | Pump not priming | Liquid drained or syphoned from system | Fit check or foot valve to prevent draining
Centrifugal Pump | Pump not priming | Worn pump impeller | Inspect, increasing pump speed might help, also fitting foot valve
Centrifugal Pump | No discharge | Lack of prime (see also above) | Open all vent cocks to release trapped air and fill pump and suction pipe completely with fluid
Centrifugal Pump | No discharge | Excessive suction lift | Check pump inlet for clogging etc. causing excessive frictionhead
Centrifugal Pump | No discharge | Excessive discharge head | Check that valves are open
Centrifugal Pump | No discharge | Excessive discharge head | Check piping for obstructions or blockage
Centrifugal Pump | No discharge | Excessive discharge head | Check total head
Centrifugal Pump | No discharge | Speed too low | Check that pump rev/min is consistent with manufacturer’s recommendations
Centrifugal Pump | No discharge | Pump clogged | Check that impeller is not clogged
Centrifugal Pump | No discharge | Wrong direction of rotation | Check that pump is running in the correct direction
Centrifugal Pump | No discharge | Vapour lock | Bleed suction pipe to clear air lock
Centrifugal Pump | No discharge | Vapour lock | Check that suction pipe is properly submerged
Centrifugal Pump | No discharge | Relief valve not properly adjusted | Check adjustment, check for dirt on valve seat
Centrifugal Pump | No discharge | Air leak | Check seals, check line(s) for air leaks
Centrifugal Pump | Low delivery | Air leaks | Check suction piping and pump for air leaks
Centrifugal Pump | Low delivery | Air leaks | Check pump gaskets
Centrifugal Pump | Low delivery | Vapour lock | Check NPSH and fluid temperature to ensure that liquid in suction line is not ‘flashing’
Centrifugal Pump | Low delivery | Low NPSH or damage | As above & also check suction pipe, foot valve etc
Centrifugal Pump | Low delivery | Clogged strainer(s) | Check and clean if necessary
Centrifugal Pump | Low delivery | Excessive inlet friction | Suction line too small, or too many fittings adding fluid friction
Centrifugal Pump | Low delivery | Relief valve incorrectly set or jammed | Check and adjust as necessary
Centrifugal Pump | Low delivery | Excessive system back pressure | Reduce system friction by re-design
Centrifugal Pump | Low delivery | Worn impeller | Inspect and replace if necessary
Centrifugal Pump | Low delivery | Worn wear rings | As above
Centrifugal Pump | Low delivery | Wrong direction of rotation | Check against manufacturer’s specification
Centrifugal Pump | Low delivery | Construction in suction line | Check that foot valve size is adequate (if fitted)
Centrifugal Pump | Low delivery | Construction in suction line | Check for other possible obstruction
Centrifugal Pump | Low delivery | Wrong pump size | Check that pump is adequate for the job
Centrifugal Pump | Low delivery | Poor suction | Checksuction pipe is properly submerged and in best position
Reciprocating Pump | Low delivery | High fluid viscosity | Check that fluid viscosity is consistent with anticipated performance
Reciprocating Pump | Low delivery | Excessive fluid temperature | Reduce speed and/or delivery, decrease suction head
Reciprocating Pump | Low delivery | Speed too low | Check operating rev/min against specification for pump performance
Reciprocating Pump | Over-heating | Stuffing box over-heats | Check that packing is not too tightly or badly fitted
Reciprocating Pump | Over-heating | Stuffing box over-heats | Check packing lubricant (where possible)
Reciprocating Pump | Over-heating | Stuffing box over-heats | Check that packing is consistent with manufacturer’s specification
Reciprocating Pump | Over-heating | Stuffing box over-heats | Check cooling flow (where applicable)
Reciprocating Pump | Over-heating | Bearings over-heating | Check oil level or lubricant condition
Reciprocating Pump | Over-heating | Bearings over-heating | Check if correct lubricant is being used
Reciprocating Pump | Over-heating | Bearings over-heating | Check bearing for misalignment or excessive tightness
Reciprocating Pump | Over-heating | Bearings over-heating | Check fitting and condition of oil seals
Reciprocating Pump | Over-heating | Bearings over-heating | Check that operating speed is not excessive
Reciprocating Pump | Over-heating | Fluid too viscous | Reduce fluid viscosity (eg by heating)
Reciprocating Pump | Over-heating | Excessive pressure | Reduce pump speed, increase delivery line size(s)
Reciprocating Pump | Vibration and noise | Cavitation | Check pump operating conditions
Reciprocating Pump | Vibration and noise | Excessive fluid viscosity | Check product suitability
Reciprocating Pump | Vibration and noise | Entrained air | Check for air leaks
Reciprocating Pump | Vibration and noise | High vapour pressure fluid | Check product/pump suitability
Reciprocating Pump | Vibration and noise | Improper pump assembly | Check and rectify
Reciprocating Pump | Vibration and noise | Unbalanced impeller | Check that impeller is not damaged or clogged
Reciprocating Pump | Vibration and noise | Misalignment | Check alignment with driver
Reciprocating Pump | Vibration and noise | Non-rigid mount | Check mounting for rigidity
Reciprocating Pump | Vibration and noise | Bent shaft, faulty bearings | Check and replace if necessary
Reciprocating Pump | Vibration and noise | Pump wear | Strip down and check for wear
Reciprocating Pump | Vibration and noise | Relief valve chattering | Re-adjust, repair or replace as necessary
Reciprocating Pump | Excessive wear | Misalignment | Check alignment with driver
Reciprocating Pump | Excessive wear | Out-of-balance | Check that impeller is not damaged or clogged
Reciprocating Pump | Excessive wear | Non-rigid mount | Check mounting for rigidity
Reciprocating Pump | Excessive wear | Bent shaft | Check and replace if necessary
Reciprocating Pump | Excessive wear | Lack of vibration | Check quantity and quality of lubricant
Reciprocating Pump | Excessive wear | Dirt in pump | Use filter to remove
Reciprocating Pump | Excessive wear | Corrosion | Check that pump materials are compatible with fluid being handled
Reciprocating Pump | Excessive wear | Too high operating speed | Check against manufacturer’s recommendations for fluid viscosity
Reciprocating Pump | Excessive wear | Operating pressure too high | Reduce speed or pressure, eg change in system
Reciprocating Pump | Excessive wear | Abrasives present in fluid | Check product/pump suitability
Reciprocating Pump | Pump requires excessive power | Speed too high | Check against recommended rev/min
Reciprocating Pump | Pump requires excessive power | Misalignment | Check alignment of pump and driver, also foundations
Reciprocating Pump | Pump requires excessive power | Internal friction | Check for rubbing contact, clogging etc
Reciprocating Pump | Pump requires excessive power | Tight bearings | Check bearings and packings (bearing temperature will be a clue)
Reciprocating Pump | Pump requires excessive power | Lack of lubrication | Check quantity and quality of lubricants
Reciprocating Pump | Pump requires excessive power | High fluid viscosity | Check that fluid viscosity is not too high for economic handling
Reciprocating (Piston) pump | No discharge | Not primed | Prime
Reciprocating (Piston) pump | No discharge | Not primed | Open vents on discharge side to release trapped air and leave open until all air is discharged
Reciprocating (Piston) pump | No discharge | Excessive suction lift | Reduce suction lift or reduce suction friction with larger diameter pipe or eliminate bends etc
Reciprocating (Piston) pump | No discharge | Air leaks | Check system and eliminate air leaks by sealing etc
Reciprocating (Piston) pump | No discharge | Vapour-bound | Check fluid temperature and vapour pressure - fluid temperature may be too high, or suction lift excessive for fluid temperature | - | fluid
Reciprocating (Piston) pump | No discharge | Blockage | Check for blockage in suction pipe, foot valve or strainer
Reciprocating (Piston) pump | No discharge | Blockage | Check pump suction valves
Reciprocating (Piston) pump | No discharge | Deterioration | Check suction valves, piston packing, piston rod packing, worn valves or badly scored cylinder
Reciprocating (Piston) pump | Low discharge pressure | Low steam pressure | Check for obstruction, leak or partially closed valve in steam system
Reciprocating (Piston) pump | Low discharge pressure | Tight packing | Loosen gland until leakage is apparent
Reciprocating (Piston) pump | Low discharge pressure | Excessive backpressure | Check that pump is not operating against excessive system head
Reciprocating (Piston) pump | Low discharge pressure | Deterioration | Check cylinder bore for wear, also condition of piston packings and valves
Reciprocating (Piston) pump | Pump stops or hesitates | Intermittent steam supply | Check for blockage etc
Reciprocating (Piston) pump | Pump stops or hesitates | Valve trouble | Check for excessive valve wear and leakage
Reciprocating (Piston) pump | Pump stops or hesitates | Valve trouble | Check that valve timing is correct
Reciprocating (Piston) pump | Pump stops or hesitates | Excessive back pressure | Check that system head is not excessive
Reciprocating (Piston) pump | Variable delivery | Air leaks | Check system for air leaks
Reciprocating (Piston) pump | Variable delivery | Misalignment | Check alignment of pump and possible distortion due to unsupported piping connected to pump cylinder
Reciprocating (Piston) pump | Variable delivery | Excessive suction lift | Reduce suction lift or reduce suction friction with larger diameter pipe or eliminate bends etc
Reciprocating (Piston) pump | Variable delivery | Vapour-bound | Reduce fluid temperature, or reduce suction lift
Reciprocating (Piston) pump | Variable delivery | Tight packing | Loosen gland
Reciprocating (Piston) pump | Variable delivery | Excessive speed | Check that operating speed is consistent with specification
Reciprocating (Piston) pump | Pump short strokes | Excessive cushioning | Adjust cushioning valves to obtain stroke
Reciprocating (Piston) pump | Pump short strokes | Worn valve | Check valve for leakage, re-face as necessary
Reciprocating (Piston) pump | Pump short strokes | Entrained gas | Modify suction intake as necessary
Reciprocating (Piston) pump | Pump short strokes | Incorrect valve timing | Check against specification and adjust as necessary
Reciprocating (Piston) pump | Pump short strokes | Worn bore | Replace liner, or re-bore and fit oversize piston
Reciprocating (Piston) pump | Piston short-strokes | Excessive cushioning | Adjust cushioning valves to obtain correct stroke
Reciprocating (Piston) pump | Piston short-strokes | Worn valve | Check valve for leakage, re-face as necessary
Reciprocating (Piston) pump | Piston short-strokes | Entrained gas | Modify suction intake as necessary
Reciprocating (Piston) pump | Piston short-strokes | Incorrect valve timing | Check against specification and adjust as necessary
Reciprocating (Piston) pump | Piston short-strokes | Worn bore | Replace liner, or re-bore and fit oversize piston
Reciprocating (Piston) pump | Piston over-strokes (hits head) | Cushion valves | Close down as necessary to reduce stroke
Reciprocating (Piston) pump | Piston over-strokes (hits head) | Piston leakage | Replace piston packing, replace worn liner or re-bore cylinder
Reciprocating (Piston) pump | Piston over-strokes (hits head) | Valve leakage | Check valves on liquid head for leakage, re-grind or re-set if necessary
Reciprocating (Piston) pump | Excessive wear | Misalignment | Check alignment
Reciprocating (Piston) pump | Excessive wear | Bent piston rod | Check for straightness
Reciprocating (Piston) pump | Excessive wear | Worn bore | Replace liner or re-bore
Reciprocating (Piston) pump | Excessive wear | Fluid | Check that pump is compatible with fluid being handled